## Monthly_Ops_Data
| Wastewater Sludge (WWS) Biogas Collection |  |  |  | Cogeneration Consumption3 |  | Electricity Consumption
Reporting Month-Year | Biogas Produced (ft3) | Biogas Temp (Avg, ⁰F) | WWS Biogas Produced1 (ft3 @ 60oF) | Methane Content2 (%V/V (CH4/biogas)) | Facility Use of Facility Biogas in Cogeneration3 (MMBtu, HHV) | Facility Use of Utility-sourced NG in Cogeneration3 (MMBtu, HHV) | Total Facility4 (kWh) | Total Facility4 (kWh) | Estimated Digester Process (kWh) | Estimated Biogas Purification Process (kWh)
2022-06-01 | 40956400 | 84.9816 | 39077876.34 | 64.63% | 16868.755 | 5282.4 | 2436440 | 2099041.4828
2022-07-01 | 35668050 | 88.0638 | 33840578.635 | 65.54% | 13103.4632 | 16481.088 | 1565950 | 1647016.3871
2022-08-01 | 39117380 | 82.9135 | 37465465.6652 | 63.48% | 3812.8385 | 19459.227 | 1841191 | 2061029.3129
2022-09-01 | 37584860 | 83.4895 | 35959486.7707 | 62.76% | 1715.93 | 2335.23 | 3909917 | 3848302.751
2022-10-01 | 42564520 | 87.9375 | 40393017.4457 | 64.69% | 14326.298 | 106.02 | 3141058 | 3297829.412
2022-11-01 | 44073140 | 80.297 | 42416488.1016 | 64.59% | 14715.756 | 158.1 | 3180126 | 2870482.0995
2022-12-01 | 45629422 | 72.1765 | 44584780.0911 | 63.76% | 9371.35 | 5948.28 | 2653409 | 2621919.9662
2023-01-01 | 45952980 | 69.2616 | 45148371.3928 | 64.59% | 17180.472 | 5408.88 | 2001355 | 1944701.7823
2023-02-01 | 42762610 | 64.2783 | 42413460.4661 | 63.28% | 17196.656 | 4144.08 | 1636294 | 1590218.289
2023-03-01 | 48984260 | 66.8554 | 48346514.6549 | 63.63% | 20553.75 | 1458.24 | 1729483 | 1877590.64
2023-04-01 | 45296370 | 73.6038 | 44140892.529 | 63.21% | 18514.944 | 3644.67 | 1998972 | 2075553.5203
2023-05-01 | 47856640 | 77.8722 | 46265534.0725 | 63.68% | 21741.339 | 1637.73 | 2230582 | 2132465.8052
2023-06-01 | 45464980 | 79.5696 | 43815036.2698 | 62.59% | 22246.796 | 1722.36 | 1534478 | 1606419.7345
2023-07-01 | 43903000 | 88.95 | 41586322.9002 | 65.05% | 21489.963 | 4594.2 | 1719353 | 1814398.011
2023-08-01 | 37311070 | 90.1015 | 35268214.4123 | 65.95% | 19167 | 3222.45 | 2012976 | 2058099.7683
2023-09-01 | 38175700 | 87.3141 | 36269388.4533 | 66.6% | 18631 | 2725.83 | 2240798 | 2230794.038
2023-10-01 | 41061790 | 78.625 | 39641079.1002 | 65.94% | 20114 | 3264.3 | 2051712 | 2106172.16
2023-11-01 | 43144940 | 72.7619 | 42110824.8268 | 62.87% | 23773 | 1574.49 | 1827806 | 1707558.5785
2023-12-01 | 48191730 | 70.336 | 47251943.2984 | 63.12% | 21536 | 1113.21 | 2096863 | 2131137.5295
2024-01-01 | 41329480 | 70.3096 | 40525531.4996 | 63.73% | 18023 | 2512.86 | 2415161 | 2282024.4614
2024-02-01 | 49204470 | 61.4536 | 49067252.5853 | 63.48% | 25578 | 2514.72 | 1437689 | 1169366.9367
2024-03-01 | 49830980 | 64.8529 | 49369978.3849 | 63.8% | 27726 | 3301.5 | 1287411 | 1404199.8424
2024-04-01 | 49448720 | 67.4125 | 48753348.4664 | 63.5% | 26251 | 5314.02 | 982152 | 1047174.315
2024-05-01 | 51517810 | 75.3161 | 50042945.1161 | 63.81% | 24423 | 5514.9 | Not yet available | 1183288.3018
2024-06-24 | 46708610 | 85.9 | 44493924 |  | 24225 | 5515 |  | 1178729.2541
2024-07-24 | 44928250 | 90 | 42479751 |  | 22223 | 5082 |  | 1439500.1034
2024-08-24 | 39574912 | 88.9 | 37490564 |  | 17343 | 3085
1Source: SW Daily Log Sheets, then converted using the following conversion process:
Rotary displacement gas flowmeters measure gas production from each of the eight individual digesters. At the Sludge Digester Tanks, the gas totalizers are read and recorded every morning at 7 am by an operator. The difference between the current day’s 7 am reading and the previous day’s 7 am reading is used to quantify gas production for the previous day (cubic feet).
Charles' Law { V2= (V1/T1) * T2 } to approximate the biogas volume at 60 ⁰F.
2Source: Ameresco’s portal, which is recorded using an ultrasonic flowmeter (FIT-1440B) that is also equipped with a % methane sensor. The data was collected in 30-minute averages and rolled up into a monthly average.
3Source: Cogen Production tracking spreadsheet prepared for DOE's EIA-923 M Report.
4Source: PECO Electricity Bill.
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Measured at Digester Building
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Measured at Cogen, after compression, before dehydration skid
Note on D3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note: these volumes have already been adjusted for temperature